## Residential
Comparative Analysis of 2026 FBC-EC 9th Edition and its effect on FELLC and operating procedures
2023 FBC-8th Edition |  | 2026 FBC-9th Edition |  | Analysis | Business Effect | Customer Comm. Req’d?
Section | Requirement | Section | Requirement
R401.2 | Compliance | R401.2 | Compliance | Adds requirement to comply with new Section R407—Additional Efficiency Requirements to compliance option #1 (increases prescriptive compliance stringency). | Energy Calculations must now comply with R 407 and will result in increased efficiency requirements for residential structures | Yes
Table R402.1.2 | Insulation and Fenestration Requirements by Component: Skylight U-factor | Table R402.1.2 | Insulation and Fenestration Requirements by Component: Skylight U-Factor | Reduces maximum skylight U-factor from 0.75 to 0.60 for Climate Zone 1 and from 0.65 to 0.60 for Climate Zone 2. | Skylights need to allow lesser heat in for Climate Zones 1 and 2; Unchanged for balance of the zones | No
|  | Table R402.1.2 | Insulation and Fenestration Requirements by Component: Skylight SHGC | Adds Skylight SHGC column and specifies a maximum skylight SHGC of 0.28 for both Climate Zones 1 and 2 (reducing maximum skylight SHGC from 0.30 for both climate zones in 2023 8th Edition). | Skylights need to allow lesser heat in for Climate Zones 1 and 2; Unchanged for balance of the zones | No
Table R402.1.2 | Insulation and Fenestration Requirements by Component: Wood Frame Wall R-value | Table R402.1.2 | Insulation and Fenestration Requirements by Component: Wood Frame Wall R-value | Adds continuous insulation R-value options to Wood Frame Wall R-value column insulation minimums for Climate Zones 1 and 2 and adds revised footnote “e” which now states that the first value shown is for cavity insulation and second value shown is for continuous | New method of insulation now permitted. EC will need to take into account correct wall build-up. Typ. Structural wall section to be modified to allow these options. | No
|  | R403.6.5 | Intermittent exhaust control for bathrooms and toilet rooms | New section specifies control requirement options for exhaust systems designed for intermittent operation serving bathrooms or toilet rooms. An exception is provided for bathroom and toilet room exhaust systems serving as integral components of outdoor air ventilation systems or whole-house mechanical ventilation systems. | High end houses w/ Saunas etc. will need new operations sequence specified | No
R403.7.1.1 | Cooling equipment capacity | R403.7.1.1 | Cooling equipment capacity | Revises section to require cooling only equipment capacity selection to be in accordance with Section R403.7.1 and according to one of three options: Option A: Requires that in accordance with ACCA Manual S, the total capacity not be less than the calculated total load but also not more than specified maximums based on whether the equipment is single stage, two stage, or multi-stage. Option B: Requires that in accordance with ACCA Manual S, the sensible capacity not be less than the calculated sensible load but also not more than 1.20 times greater than the sensible load. Also requires that the latent capacity not be less than the calculated latent load. Option C: For sizing based on Manual J, a permanently installed supplementary unit is permitted to meet the calculated latent load (includes primary unit total capacity requirements and primary plus supplemental unit latent capacity requirements). This option also requires the efficiency rating of the supplementary unit to be included as proposed per Table R405.5.2.(1) and R406.4, and that a provided notice regarding the unit be installed on the air handler.
|  | R407 | Additional Efficiency Requirements | New section added specifying additional efficiencies and credits available | EC to be updated per new requirements for additional credits if required by Homeowner, especially Building Thermal envelopes.
|  | R407.2.2 | More Efficient HVAC Equipment performance Options | New section provides requirements for obtaining heating and cooling equipment credit, including cooling with electric resistance heating, cooling with gas heating, and air source heat pump options (for Section R407 additional efficiency requirements for prescriptive compliance). | Increases Equipment Efficiency to 15.2SEER2 for Electric Heating and 78HSPF2/15.2SEER2 Air Source Heat Pump. | Yes, for high end arch

## Commercial
Comparative Analysis of 2026 FBC-EC 9th Edition and its effect on FELLC and operating procedures
2023 FBC-8th Edition |  | 2026 FBC-9th Edition |  | Analysis | Business Effect | Customer Comm. Req’d?
Section | Requirement | Section | Requirement
Table C402.4 | Building Envelope Fenestration Maximum U-Factors and SHGC Requirements | Table C402.4 | Building Thermal Envelope Fenestration Maximum U-Factors and SHGC Requirements | Increased the stringency of vertical fenestration: U-Factors in climate zones 1 and 2 and SHGC in climate zone1 only. Also increased the stringency of U-factors and SHGC for sky lights in climate zone 1. | Lower HVAC sizes requiring more custom units for High OA applications
C402.5.1.2 | Air barrier compliance | C402.5.1.2 | Air leakage compliance | The revised provision increased the stringency of measured air leakage rate from 0.40 to 0.35 cfm/ft2 at 0.3 inch of water gauge for all buildings and as an alternative added a measured leakage rate threshold of 0.27 cfm/ft2 at 0.2 inch of water gauge for Group I-1 and Group R-1 buildings if tested by an approved third party. | Lower HVAC sizes requiring more custom units for High OA applications; Potentially higher construction costs
Table C403.2.3(1) | Minimum Efficiency Requirements: Electrically Operated Unitary Air Conditioners AND Condensing Units | Table C403.2.3(1) | Minimum Efficiency Requirements: Electrically Operated Unitary Air Conditioners AND Condensing Units | Air conditioners (air-cooled): For a single packaged system, all heating types, and capacity < 65 kBtu/h SEER2 increased to 13.8 from 13.4 after 1/1/2023 | No major change affecting existing standards in use
Table C403.2.3(11) | Minimum Efficiency Requirements Variable Refrigerant Flow Multi-Split Air Conditioners and Heat Pumps | Table C403.2.3(11) | Electronically Operated Variable Refrigerant Flow Multi-Split Air Conditioners—Minimum Efficiency Requirements | The minimum EER values for cooling capacities ≥ 65 kBtu/h are less stringent in the 2026 FBC-EC compared to the 2023 FBC-EC values. However, the IEER values remain the same for all capacity range. The minimum efficiency VRF multi-split ACs, electric resistance or none heating type, and capacity range ≥ 65 kBtu/h and < 135 kBtu/h reduced to EER 10.5 from EER 11.0. | Wider range of units available to select
|  |  |  | The minimum efficiency requirement for VRF multi-split ACs, electric resistance or none heating type, and capacity range ≥ 135 kBtu/h and <240 kBtu/h reduced to EER 10.3 from EER 11.0. | Wider range of units available to select